## Slide 1: OPC UA EPICS Device Support
Demo / Hands-On Instructions
Ralph Lange

## Slide 2: Manual Integration Workflow Step 1: Browse the Server
Free browsing tool: UaExpert

## Slide 3: Manual Integration Workflow Step 2: Configure the IOC
Configure the OPC UA server connections from the startup script
Add an EPICS record to your database
    opcuaSession PLC1 opc.tcp://plc1.controls.local:4840 sec-mode=None
    opcuaSubscription SUB1 PLC1 200
    record(ai, "$(DEVICE):dbl1") {
    field(DTYP, "OPCUA")
    field(INP, "@SUB1 ns=3;s=\"Data_block_1\".\"myDouble\"")
    field(PREC, "3")
    }

## Slide 4: Manual Integration Workflow Step 3: Design Your Client Applications and Connect

## Slide 5: Log Onto the Training-VM

## Slide 6: Start the Demo Server
Open a new terminal
Unpack the Unified Automation demo server
Run it
  Use CTRL-C and restart it to simulate an orderly server disconnect and reconnect
  Use CTRL-Z and “fg” to simulate network hang-up

## Slide 7: Start the UaExpert Browser
The first start requires you to create a self-signed certificate. Just enter any data.

## Slide 8: UaExpert: Add the Demo Server
Select Server, then Add…
Use the Advanced tab and enter the endpoint URL
opc.tcp://localhost:48010

## Slide 9: UaExpert: Connect
Connect by clicking on the Connect Server icon
Trust the unknown self-signed server certificate
and Continue

## Slide 10: UaExpert: Familiarize Yourself
Browse
Inspect
Monitor

## Slide 11: Build the IOC Two Steps
Change directory into the application cd training/opcua-support
Build the example IOC make

## Slide 12: Run the IOC
Change into the IOC’s startup directory
Run the IOC binary, giving the name of the startup file as argument
Using a subshell avoids having to change directory all the time
( cd iocBoot/iocUaDemoServer/; ../../bin/linux-x86_64/opcuaIoc st.cmd )
Always do a clean exit of the IOC, using CTRL-D or the exit command OPC UA servers don’t free their session resources when a connection breaks – if the same session is reconnected, it just continues

## Slide 13: Run the IOC

## Slide 14: Add Your Own Stuff The Fun Part
Add a line to the DeviceDbApp/UaDemoServerDb/Makefile: DB += myOwnStuff.db
Add a line to iocBoot/iocUaDemoServer/st.cmd to load your database: dbLoadRecords "db/myOwnStuff.db"
Create DeviceDbApp/UaDemoServerDb/myOwnStuff.db and add your records
After changing the database file, don’t forget to run make again before booting your IOC
Check your stuff by creating a Phoebus display or by using command line tools: caput, caget, camonitor

## Slide 15: Add Your Own Stuff Ideas for More Fun
The items under “000_Static” are mailboxes link output records and input records and manipulate their values
The items under “001_Dynamic” are updated by the server monitored input records will show the value changes
The items under “015_WorkOrder” have user-defined structured data use the setup for structures (using opcuaItemRecord) to link them
The “Cheat Sheet” document (in the presentations folder) lists all available options for the record configuration
  Add a second subscription (slow) and use a server-side queue to avoid losing any updates Check the difference between IOC and OPC UA time stamps

## Slide 16: Thanks for Your Attention!
Any questions left unanswered?
OPC UA room on EPICS Chat